## MESA-PCS
Modular Energy Storage Architecture
Power Conversion System Extensions for Energy Storage
2014-10-01
Draft 2
DRAFT
This document contains information regarding to the MESA-PCS extentions to the SunSpec inverter models. These extensions allow a four-quadrant PCS to operate effectively in a MESA-compatible Energy Storage System.
The MESA-PCS extensions are implemented as a vendor-specific SunSpec model. The details of this model can be found on the V 64800 tab in this workbook. Additional information can be found in the companion document "MESA-PCS Specification".

## V 64800
// MESA-PCS Extensions Model
Start Offset | End Offset | Size | R/W | Name | Label | Type | Units | SF | Description | Notes | M/O | PICS (Y, N) | Comment/Value
1 | 1 | 1 | R | ID |  | unit16 |  |  | A well-known value 64800. Uniquely identifies this as a MESA-PCS Extensions Model |  | M
2 | 2 | 1 | R | L |  | uint16 |  |  | Well-known # of 16-bit registers to follow : 14 |  | M
// MESA-PCS Extensions: Fixed Block (14)
3 | 3 | 1 | R | LocRemCtl | Control Mode | enum16 |  |  | Inverter control mode. Enumeration. |  | M |  | Maps to DRCC.LocRemCtl.
4 | 4 | 1 | R | PCSHb | PCS Heartbeat | uint16 |  |  | Value is incremented every second with periodic resets to zero. |  | O
5 | 5 | 1 | RW | ControllerHb | Controller Heartbeat | uint16 |  |  | Value is incremented every second with periodic resets to zero. |  | O
6 | 6 | 1 | RW | PCSAlarmReset | Alarm Reset | uint16 |  |  | Used to reset any latched alarms. 1 = Reset. |  | O
7 | 7 | 1 | RW | PCSSetOperation | Set Operation | enum16 |  |  | Commands the PCS. Enumerated value. |  | M
8 | 8 | 1 | RW | MaxBatACha | Charge Current Limit | uint16 | A | MaxBatA_SF | Instantaneous maximum DC charge current. | From battery. | O |  | Compare to ZBAT.MaxBatA. Follow up with IEC 61850 required.
9 | 9 | 1 | RW | MaxBatADischa | Discharge Current Limit | uint16 | A | MaxBatA_SF | Instantaneous maximum DC discharge current. | From battery. | O |  | Compare to ZBAT.MaxBatA. Follow up with IEC 61850 required.
10 | 10 | 1 | R | MaxA | AC Maximum Current Limit | uint16 | A | MaxA_SF | Nameplate maximum AC charge/discharge current. |  | O
11 | 11 | 1 | R | MaxACur | AC Maximum Current Limit Percentage | uint16 | % | MaxACur_SF | Instantaneous maximum AC charge/discharge current, expressed as a percentage of MaxA. |  | O
12 | 12 | 1 | R | MaxBatA_SF |  | sunssf |  |  | Scale factor for instantationous DC charge/discharge current. |  | O
13 | 13 | 1 | R | MaxA_SF |  | sunssf |  |  | Scale factor for nameplate maximum AC charge/discharge current. |  | O
14 | 14 | 1 | R | MaxACur_SF |  | sunssf |  |  | Scale factor for instantaneous maximum AC charge/discharge current percentage. |  | O
15 | 15 | 1 | R | Padding 1 |  | pad |  |  |  |  | M
16 | 16 | 1 | R | Padding 2 |  | pad |  |  |  |  | M
// LocRemCtl enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
REMOTE |  |  | 0 |  | Remote Control |  | PCS is controlled remotely (e.g. by the upstream controller)
LOCAL |  |  | 1 |  | Local Control |  | PCS is controlled by a local operator (e.g. through PCS HMI) |  | Local mode is required for manual/maintenance operations. Once invoked, it must be explicitly exited for the inverter to be controlled remotely.
// PCSSetOperation enumerated values
ID |  |  | Value |  | Label |  | Description |  | Notes |  | PICS (Y/N) | Comment
START |  |  | 1 |  | Start the PCS |  | AC breaker and DC contactor are closed upon successful start.
STOP |  |  | 2 |  | Stop the PCS |  | AC breaker and DC contactor are open on shutdown.
ENTER STANDBY |  |  | 3 |  | Enter Standby Mode
EXIT STANDBY |  |  | 4 |  | Exit Standby Mode