## License Agreement
SunSpec Alliance
SunSpec Infomation Model Reference
Date Generated: 2017-09-13
This document is generated programatically from the canonical model definitions contained in the SunSpec model repository.
For the most up-to-date version of this document, go to: www.sunspec.org/download
Copyright SunSpec Alliance 2009-2015. All Rights Reserved.
This document and the information contained herein is provided on an "AS IS" basis and the SunSpec Alliance DISCLAIMS ALL WARRANTIES, EXPRESS OR IMPLIED, INCLUDING BUT NOT LIMITED TO ANY WARRANTY THAT THE USE OF THE INFORMATION HEREIN WILL NOT INFRINGE ANY OWNERSHIP RIGHTS OR ANY IMPLIED WARRANTIES OF MERCHANTABILITY OR FITNESS FOR A PARTICULAR PURPOSE.
This document may be used, copied, and furnished to others, without restrictions of any kind, provided that this document itself may not be modified in anyway, except as needed by the SunSpec Technical Committee and as governed by the SunSpec IPR Policy. The complete policy of the SunSpec Alliance can be found at www.sunspec.org.
Prepared by the SunSpec Alliance
4030 Moorpark Avenue, Suite 109
San Jose, CA 95117
Website: www.sunspec.org
Email: info@sunspec.org

## Summary
Summary
This spreadsheet describes SunSpec Alliance Data Models and Modbus maps.
Each spreadsheet tab describes an individual data model of one of the following types:
Id Range | Model Type
1 | Common
2 | Aggregator
010 to 019 | Network Configuration
100 series | Inverter
200 series | Meter
300 series | Environmental
400 series | String Combiner
500 series | Panel
600 series | Tracker
700 series | Reserved by SunSpec Alliance
800 series | Storage
900 - 63000 | Reserved by SunSpec Alliance
64000 series | Vendor Specific
This document includes data models that are of Approved, Test, and Draft status.
Before using any of these models, please check the release status of the model in question.
Only Approved models may be SunSpec Certified.
Canonical Representation
The documentation contained in this spreadsheet is derived from SunSpec Model Definition XML (SMDX) files, which can be downloaded from www.sunspec.org/modelreference/
Please note that the SMDX files are the canonical (definitive) representations of SunSpec models.
SunSpec Specification Documentation
All current SunSpec specifications (PDF format) are available for free downloading at http://sunspec.org/download/.
SunSpec Certification
If you would like to have your product SunSpec Certified, please read the information available at http://sunspec.org/sunspec-certified-program/
and then email certification@sunspec.org to schedule your test.

## Index
Model | Label | Description | Notes
801 | Energy Storage Base Model (DEPRECATED) | This model has been deprecated.
802 | Battery Base Model
803 | Lithium-Ion Battery Bank Model
804 | Lithium-Ion String Model
805 | Lithium-Ion Module Model
806 | Flow Battery Model
807 | Flow Battery String Model
808 | Flow Battery Module Model
809 | Flow Battery Stack Model

## 801
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Energy Storage Base Model (DEPRECATED) | 801 | uint16 |  |  | R | M | This model has been deprecated.
Header |  | 1 |  | 1 | L |  | 1 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | DEPRECATED | Deprecated Model |  | enum16 |  |  | R | M | This model has been deprecated.

## 802
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Battery Base Model | 802 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 62 | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | AHRtg | Nameplate Charge Capacity |  | uint16 | Ah | AHRtg_SF | R | M | Nameplate charge capacity in amp-hours.
Fixed Block |  | 3 | 1 | 1 | WHRtg | Nameplate Energy Capacity |  | uint16 | Wh | WHRtg_SF | R | M | Nameplate energy capacity in DC watt-hours.
Fixed Block |  | 4 | 2 | 1 | WChaRteMax | Nameplate Max Charge Rate |  | uint16 | W | WChaDisChaMax_SF | R | M | Maximum rate of energy transfer into the storage device in DC watts.
Fixed Block |  | 5 | 3 | 1 | WDisChaRteMax | Namplate Max Discharge Rate |  | uint16 | W | WChaDisChaMax_SF | R | M | Maximum rate of energy transfer out of the storage device in DC watts.
Fixed Block |  | 6 | 4 | 1 | DisChaRte | Self Discharge Rate |  | uint16 | %WHRtg | DisChaRte_SF | R | O | Self discharge rate. Percentage of capacity (WHRtg) discharged per day.
Fixed Block |  | 7 | 5 | 1 | SoCMax | Nameplate Max SoC |  | uint16 | %WHRtg | SoC_SF | R | O | Manufacturer maximum state of charge, expressed as a percentage.
Fixed Block |  | 8 | 6 | 1 | SoCMin | Nameplate Min SoC |  | uint16 | %WHRtg | SoC_SF | R | O | Manufacturer minimum state of charge, expressed as a percentage.
Fixed Block |  | 9 | 7 | 1 | SocRsvMax | Max Reserve Percent |  | uint16 | %WHRtg | SoC_SF | RW | O | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 10 | 8 | 1 | SoCRsvMin | Min Reserve Percent |  | uint16 | %WHRtg | SoC_SF | RW | O | Setpoint for maximum reserve for storage as a percentage of the nominal maximum storage.
Fixed Block |  | 11 | 9 | 1 | SoC | State of Charge |  | uint16 | %WHRtg | SoC_SF | R | M | State of charge, expressed as a percentage. | Measurement.
Fixed Block |  | 12 | 10 | 1 | DoD | Depth of Discharge |  | uint16 | % | DoD_SF | R | O | Depth of discharge, expressed as a percentage. | Measurement.
Fixed Block |  | 13 | 11 | 1 | SoH | State of Health |  | uint16 | % | SoH_SF | R | O | Percentage of battery life remaining.
Fixed Block |  | 14 | 12 | 2 | NCyc | Cycle Count |  | uint32 |  |  | R | O | Number of cycles executed in the battery.
Fixed Block |  | 16 | 14 | 1 | ChaSt | Charge Status |  | enum16 |  |  | R | O | Charge status of storage device. Enumeration.
Fixed Block |  | 17 | 15 | 1 | LocRemCtl | Control Mode |  | enum16 |  |  | R | M | Battery control mode. Enumeration. | Maps to DRCC.LocRemCtl in IEC 61850.
Fixed Block |  | 18 | 16 | 1 | Hb | Battery Heartbeat |  | uint16 |  |  | R | O | Value is incremented every second with periodic resets to zero.
Fixed Block |  | 19 | 17 | 1 | CtrlHb | Controller Heartbeat |  | uint16 |  |  | RW | O | Value is incremented every second with periodic resets to zero.
Fixed Block |  | 20 | 18 | 1 | AlmRst | Alarm Reset |  | uint16 |  |  | RW | M | Used to reset any latched alarms. 1 = Reset. | Battery should reset to 0 when reset is complete.
Fixed Block |  | 21 | 19 | 1 | Typ | Battery Type |  | enum16 |  |  | R | M | Type of battery. Enumeration. | Maps to DBAT.BatTyp in 61850.
Fixed Block |  | 22 | 20 | 1 | State | State of the Battery Bank |  | enum16 |  |  | R | M | State of the battery bank. Enumeration. | Must be reconciled with State in IEC 61850.
Fixed Block |  | 23 | 21 | 1 | StateVnd | Vendor Battery Bank State |  | enum16 |  |  | R | O | Vendor specific battery bank state. Enumeration.
Fixed Block |  | 24 | 22 | 2 | WarrDt | Warranty Date |  | uint32 |  |  | R | O | Date the device warranty expires. | Number of days since 1/1/2000.
Fixed Block |  | 26 | 24 | 2 | Evt1 | Battery Event 1 Bitfield |  | bitfield32 |  |  | R | M | Alarms and warnings. Bit flags.
Fixed Block |  | 28 | 26 | 2 | Evt2 | Battery Event 2 Bitfield |  | bitfield32 |  |  | R | M | Alarms and warnings. Bit flags. | Reserved for future use.
Fixed Block |  | 30 | 28 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | M | Vendor defined events.
Fixed Block |  | 32 | 30 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | M | Vendor defined events.
Fixed Block |  | 34 | 32 | 1 | V | External Battery Voltage |  | uint16 | V | V_SF | R | M | DC Bus Voltage. | Maps to ZBAT.V in IEC 61850.
Fixed Block |  | 35 | 33 | 1 | VMax | Max Battery Voltage |  | uint16 | V | V_SF | R | O | Instantaneous maximum battery voltage. | If not implemented, must implement AChaMax and ADisChaMax.
Fixed Block |  | 36 | 34 | 1 | VMin | Min Battery Voltage |  | uint16 | V | V_SF | R | O | Instantaneous minimum battery voltage. | If not implemented, must implement AChaMax and ADisChaMax.
Fixed Block |  | 37 | 35 | 1 | CellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | O | Maximum voltage for all cells in the bank. | Measurement.
Fixed Block |  | 38 | 36 | 1 | CellVMaxStr | Max Cell Voltage String |  | uint16 |  |  | R | O | String containing the cell with maximum voltage.
Fixed Block |  | 39 | 37 | 1 | CellVMaxMod | Max Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with maximum voltage.
Fixed Block |  | 40 | 38 | 1 | CellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | O | Minimum voltage for all cells in the bank. | Measurement.
Fixed Block |  | 41 | 39 | 1 | CellVMinStr | Min Cell Voltage String |  | uint16 |  |  | R | O | String containing the cell with minimum voltage.
Fixed Block |  | 42 | 40 | 1 | CellVMinMod | Min Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with minimum voltage.
Fixed Block |  | 43 | 41 | 1 | CellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | O | Average cell voltage for all cells in the bank. | Calculation based on measurements.
Fixed Block |  | 44 | 42 | 1 | A | Total DC Current |  | int16 | A | A_SF | R | M | Total DC current flowing to/from the battery bank. | Measurement.
Fixed Block |  | 45 | 43 | 1 | AChaMax | Max Charge Current |  | uint16 | A | AMax_SF | R | O | Instantaneous maximum DC charge current. | Calculation which is always unsigned (i.e. magnitude only). If not implemented, must implement VMax and VMin.
Fixed Block |  | 46 | 44 | 1 | ADisChaMax | Max Discharge Current |  | uint16 | A | AMax_SF | R | O | Instantaneous maximum DC discharge current. | Calculation which is always unsigned (i.e. magnitude only). If not implemented, must implement VMax and VMin.
Fixed Block |  | 47 | 45 | 1 | W | Total Power |  | int16 | W | W_SF | R | M | Total power flowing to/from the battery bank. | Measurement.
Fixed Block |  | 48 | 46 | 1 | ReqInvState | Inverter State Request |  | enum16 |  |  | R | O | Request from battery to start or stop the inverter. Enumeration. | Used in special states such as manual battery charging.
Fixed Block |  | 49 | 47 | 1 | ReqW | Battery Power Request |  | int16 | W | W_SF | R | O | AC Power requested by battery. | Used in special states such as string balancing.
Fixed Block |  | 50 | 48 | 1 | SetOp | Set Operation |  | enum16 |  |  | RW | M | Instruct the battery bank to perform an operation such as connecting. Enumeration.
Fixed Block |  | 51 | 49 | 1 | SetInvState | Set Inverter State |  | enum16 |  |  | RW | M | Set the current state of the inverter. | Information needed by battery for some operations.
Fixed Block |  | 52 | 50 | Size: 1; Name: AHRtg_SF; Type: sunssf; R/W: R | M | Scale factor for charge capacity.
Fixed Block |  | 53 | 51 | Size: 1; Name: WHRtg_SF; Type: sunssf; R/W: R | M | Scale factor for energy capacity.
Fixed Block |  | 54 | 52 | Size: 1; Name: WChaDisChaMax_SF; Type: sunssf; R/W: R | M | Scale factor for maximum charge and discharge rate.
Fixed Block |  | 55 | 53 | Size: 1; Name: DisChaRte_SF; Type: sunssf; R/W: R | O | Scale factor for self discharge rate.
Fixed Block |  | 56 | 54 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | M | Scale factor for state of charge values.
Fixed Block |  | 57 | 55 | Size: 1; Name: DoD_SF; Type: sunssf; R/W: R | O | Scale factor for depth of discharge.
Fixed Block |  | 58 | 56 | Size: 1; Name: SoH_SF; Type: sunssf; R/W: R | O | Scale factor for state of health.
Fixed Block |  | 59 | 57 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Scale factor for DC bus voltage.
Fixed Block |  | 60 | 58 | Size: 1; Name: CellV_SF; Type: sunssf; R/W: R | M | Scale factor for cell voltage.
Fixed Block |  | 61 | 59 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Scale factor for DC current.
Fixed Block |  | 62 | 60 | Size: 1; Name: AMax_SF; Type: sunssf; R/W: R | M | Scale factor for instantationous DC charge/discharge current.
Fixed Block |  | 63 | 61 | Size: 1; Name: W_SF; Type: sunssf; R/W: R | O | Scale factor for AC power request.
enum16 | ChaSt |  |  | Name: OFF; Value: 1
enum16 | ChaSt |  |  | Name: EMPTY; Value: 2
enum16 | ChaSt |  |  | Name: DISCHARGING; Value: 3
enum16 | ChaSt |  |  | Name: CHARGING; Value: 4
enum16 | ChaSt |  |  | Name: FULL; Value: 5
enum16 | ChaSt |  |  | Name: HOLDING; Value: 6
enum16 | ChaSt |  |  | Name: TESTING; Value: 7
enum16 | LocRemCtl |  |  | Name: REMOTE; Label: Remote Control; Value: 0 |  | Battery is controlled remotely (e.g. by the site controller). | Value of 0 matches LocRemCtl in IEC 61850.
enum16 | LocRemCtl |  |  | Name: LOCAL; Label: Local Control; Value: 1 |  | Battery is controlled by a local operator (e.g. through battery HMI). | Value of 1 matches LocRemCtl in IEC 61850.
enum16 | Typ |  |  | Name: NOT APPLICABLE_UNKNOWN; Label: Not Applicable or Unknown; Value: 0 |  | Battery type is not applicable or unknown.
enum16 | Typ |  |  | Name: LEAD_ACID; Label: Lead-Acid; Value: 1 |  | Lead-acid battery type.
enum16 | Typ |  |  | Name: NICKEL_METAL_HYDRATE; Label: Nickel-Metal Hydrate; Value: 2 |  | Nickel-metal hydrate battery type.
enum16 | Typ |  |  | Name: NICKEL_CADMIUM; Label: Nickel-Cadmium; Value: 3 |  | Nickel-cadmium battery type.
enum16 | Typ |  |  | Name: LITHIUM_ION; Label: Lithium-Ion; Value: 4 |  | Lithium-ion battery type.
enum16 | Typ |  |  | Name: CARBON_ZINC; Label: Carbon-Zinc; Value: 5 |  | Carbon-zinc battery type.
enum16 | Typ |  |  | Name: ZINC_CHLORIDE; Label: Zinc Chloride; Value: 6 |  | Zinc chloride battery type.
enum16 | Typ |  |  | Name: ALKALINE; Label: Alkaline; Value: 7 |  | Alkaline battery type.
enum16 | Typ |  |  | Name: RECHARGEABLE_ALKALINE; Label: Rechargeable Alkaline; Value: 8 |  | Rechargeable alkaline battery type.
enum16 | Typ |  |  | Name: SODIUM_SULFUR; Label: Sodium-Sulfur; Value: 9 |  | Sodium-sulfur battery type.
enum16 | Typ |  |  | Name: FLOW; Label: Flow; Value: 10 |  | Flow battery type.
enum16 | Typ |  |  | Name: OTHER; Label: Other; Value: 99 |  | Other battery type.
enum16 | State |  |  | Name: DISCONNECTED; Label: Disconnected; Value: 1 |  | Battery bank is disconnected. All contactors are open.
enum16 | State |  |  | Name: INITIALIZING; Label: Initializing; Value: 2 |  | Battery bank is initializing but not ready for operating. String balancing may occur.
enum16 | State |  |  | Name: CONNECTED; Label: Connected; Value: 3 |  | Battery bank is ready for operation. All enabled contactors are closed.
enum16 | State |  |  | Name: STANDBY; Label: Standby; Value: 4 |  | Battery bank is connected and in standby/power saving mode.
enum16 | State |  |  | Name: SOC PROTECTION; Label: SoC Protection; Value: 5 |  | Battery bank is connected but SoC is too low. Battery should be considered "offline".
enum16 | State |  |  | Name: SUSPENDING; Label: Suspending; Value: 6 |  | Battery bank is suspending operation and will disconnect.
enum16 | State |  |  | Name: FAULT; Label: Fault; Value: 99 |  | The battery has experienced a critical failure and may not be operated.
bitfield32 | Evt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | Unable to communcate with BMS or BMS is unable to communicate with battery strings.
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Battery has exceeded maximum operating temperature
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 2 |  | Battery is approaching maximum operating temperature.
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 3 |  | Battery has exceeded minimum operating temperature
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Battery is approaching minimum operating temperature.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Battery maximum charge current has been exceeded. | See AChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 6 |  | Approaching battery maximum charge current. | See AChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 7 |  | Battery maximum discharge current has been exceeded. | See ADisChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching battery maximum discharge current. | See ADisChaMax.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Battery voltage has exceeded maximum limit.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 10 |  | Battery voltage is approaching maximum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 11 |  | Battery voltage has exceeded minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Battery voltage is approaching minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Min Alarm; Value: 13 |  | Battery state of charge has reached or exceeded SoCMin
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Min Warning; Value: 14 |  | Battery state of charge is approaching SoCMin
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Max Alarm; Value: 15 |  | Battery state of charge has reached or exceeded SoCMax
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Max Warning; Value: 16 |  | Battery state of charge is approaching SoCMax
bitfield32 | Evt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 17 |  | A voltage imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_ALARM; Label: Temperature Imbalance Alarm; Value: 18 |  | A temperature imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_WARNING; Label: Temperature Imbalance Warning; Value: 19 |  | A temperature imbalance is developing between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 20 |  | A contactor failed to open or close as requested.
bitfield32 | Evt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 21 |  | One or more battery fans has failed.
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 22 |  | Ground fault detected.
bitfield32 | Evt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 23 |  | One or more doors are open.
bitfield32 | Evt1 |  |  | Name: CURRENT_IMBALANCE_WARNING; Label: Current Imbalance Warning; Value: 24 |  | A current imbalance exists between the strings in the battery bank.
bitfield32 | Evt1 |  |  | Name: OTHER_ALARM; Label: Other Battery Alarm; Value: 25 |  | A vendor specific alarm has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: OTHER_WARNING; Label: Other Battery Warning; Value: 26 |  | A vendor specific warning has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: RESERVED_1; Label: Reserved; Value: 27 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_ALARM; Label: Configuation Alarm; Value: 28 |  | The battery bank has been configured incorrectly and will not operate.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_WARNING; Label: Configuation Warning; Value: 29 |  | The battery bank has been configured incorrectly and may not operated as expected.
enum16 | ReqInvState |  |  | Name: NO REQUEST; Label: No Request; Value: 0 |  | Battery has no requests of the inverter.
enum16 | ReqInvState |  |  | Name: START; Label: Start Inverter; Value: 1 |  | Battery requests that the inverter be started. | Battery is notified of inverter state change through SetInvState.
enum16 | ReqInvState |  |  | Name: STOP; Label: Stop Inverter; Value: 2 |  | Battery requests that the inverter be stopped. | Battery is notified of inverter state change through SetInvState.
enum16 | SetOp |  |  | Name: CONNECT; Label: Connect the Battery Bank; Value: 1 |  | Initialize the battery bank and close contactors for all enabled strings.
enum16 | SetOp |  |  | Name: DISCONNECT; Label: Disconnect the Battery Bank; Value: 2 |  | Open contactors for all strings.
enum16 | SetInvState |  |  | Name: INVERTER_STOPPED; Label: Inverter is Stopped; Value: 1
enum16 | SetInvState |  |  | Name: INVERTER_STANDBY; Label: Inverter is in Standby; Value: 2
enum16 | SetInvState |  |  | Name: INVERTER_STARTED; Label: Inverter is Started; Value: 3

## 803
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Lithium-Ion Battery Bank Model | 803 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 26 + (RB Count * 32) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | NStr | String Count |  | uint16 |  |  | R | M | Number of strings in the bank.
Fixed Block |  | 3 | 1 | 1 | NStrCon | Connected String Count |  | uint16 |  |  | R | M | Number of strings with contactor closed.
Fixed Block |  | 4 | 2 | 1 | ModTmpMax | Max Module Temperature |  | int16 |  | ModTmp_SF | R | M | Maximum temperature for all modules in the bank. | Measurement.
Fixed Block |  | 5 | 3 | 1 | ModTmpMaxStr | Max Module Temperature String |  | uint16 |  |  | R | O | String containing the module with maximum temperature.
Fixed Block |  | 6 | 4 | 1 | ModTmpMaxMod | Max Module Temperature Module |  | uint16 |  |  | R | O | Module with maximum temperature.
Fixed Block |  | 7 | 5 | 1 | ModTmpMin | Min Module Temperature |  | int16 | C | ModTmp_SF | R | M | Minimum temperature for all modules in the bank. | Measurement.
Fixed Block |  | 8 | 6 | 1 | ModTmpMinStr | Min Module Temperature String |  | uint16 |  |  | R | O | String containing the module with minimum temperature.
Fixed Block |  | 9 | 7 | 1 | ModTmpMinMod | Min Module Temperature Module |  | uint16 |  |  | R | O | Module with minimum temperature.
Fixed Block |  | 10 | 8 | 1 | ModTmpAvg | Average Module Temperature |  | uint16 |  |  | R | O | Average temperature for all modules in the bank. | Calculation based on measurements.
Fixed Block |  | 11 | 9 | 1 | StrVMax | Max String Voltage |  | uint16 | V | V_SF | R | O | Maximum string voltage for all strings in the bank. | Measurement.
Fixed Block |  | 12 | 10 | 1 | StrVMaxStr | Max String Voltage String |  | uint16 |  |  | R | O | String with maximum voltage.
Fixed Block |  | 13 | 11 | 1 | StrVMin | Min String Voltage |  | uint16 | V | V_SF | R | O | Minimum string voltage for all strings in the bank. | Measurement.
Fixed Block |  | 14 | 12 | 1 | StrVMinStr | Min String Voltage String |  | uint16 |  |  | R | O | String with minimum voltage.
Fixed Block |  | 15 | 13 | 1 | StrVAvg | Average String Voltage |  | uint16 | V | V_SF | R | O | Average string voltage for all strings in the bank. | Calculation based on measurements.
Fixed Block |  | 16 | 14 | 1 | StrAMax | Max String Current |  | int16 | A | A_SF | R | O | Maximum current of any string in the bank. | Measurement.
Fixed Block |  | 17 | 15 | 1 | StrAMaxStr | Max String Current String |  | uint16 |  |  | R | O | String with the maximum current.
Fixed Block |  | 18 | 16 | 1 | StrAMin | Min String Current |  | int16 | A | A_SF | R | O | Minimm current of any string in the bank. | Measurement.
Fixed Block |  | 19 | 17 | 1 | StrAMinStr | Min String Current String |  | uint16 |  |  | R | O | String with the minimum current.
Fixed Block |  | 20 | 18 | 1 | StrAAvg | Average String Current |  | int16 | A | A_SF | R | O | Average string current for all strings in the bank. | Calculation based on measurements.
Fixed Block |  | 21 | 19 | 1 | NCellBal | Battery Cell Balancing Count |  | uint16 |  |  | R | O | Total number of cells that are currently being balanced.
Fixed Block |  | 22 | 20 | Size: 1; Name: CellV_SF; Type: sunssf; R/W: R | M | Scale factor for cell voltage.
Fixed Block |  | 23 | 21 | Size: 1; Name: ModTmp_SF; Type: sunssf; R/W: R | M | Scale factor for module temperatures.
Fixed Block |  | 24 | 22 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Scale factor for string currents.
Fixed Block |  | 25 | 23 | Size: 1; Name: SoH_SF; Type: sunssf; R/W: R | O | Scale factor for string state of health.
Fixed Block |  | 26 | 24 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | M | Scale factor for string state of charge.
Fixed Block |  | 27 | 25 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | O | Scale factor for string voltage.
Repeating Block |  | 28 | 0 | 1 | StrNMod | Module Count |  | uint16 |  |  | R | M | Count of modules in the string.
Repeating Block |  | 29 | 1 | 2 | StrSt | String Status |  | bitfield32 |  |  | R | M | Current status of the string.
Repeating Block |  | 31 | 3 | 1 | StrConFail | Connection Failure Reason |  | enum16 |  |  | R | O
Repeating Block |  | 32 | 4 | 1 | StrSoC | String State of Charge |  | uint16 | % | SoC_SF | R | M | Battery string state of charge, expressed as a percentage. | Measurement.
Repeating Block |  | 33 | 5 | 1 | StrSoH | String State of Health |  | uint16 | % | SoH_SF | R | O | Battery string state of health, expressed as a percentage. | Measurement.
Repeating Block |  | 34 | 6 | 1 | StrA | String Current |  | int16 | A | A_SF | R | M | String current measurement. | Measurement.
Repeating Block |  | 35 | 7 | 1 | StrCellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | M | Maximum voltage for all cells in the string. | Measurement.
Repeating Block |  | 36 | 8 | 1 | StrCellVMaxMod | Max Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the maximum cell voltage.
Repeating Block |  | 37 | 9 | 1 | StrCellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | M | Minimum voltage for all cells in the string. | Measurement.
Repeating Block |  | 38 | 10 | 1 | StrCellVMinMod | Min Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the minimum cell voltage.
Repeating Block |  | 39 | 11 | 1 | StrCellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | M | Average voltage for all cells in the string. | Calculation based on measurements.
Repeating Block |  | 40 | 12 | 1 | StrModTmpMax | Max Module Temperature |  | int16 | C | ModTmp_SF | R | M | Maximum temperature for all modules in the bank. | Measurement.
Repeating Block |  | 41 | 13 | 1 | StrModTmpMaxMod | Max Module Temperature Module |  | uint16 |  |  | R | O | Module with the maximum temperature.
Repeating Block |  | 42 | 14 | 1 | StrModTmpMin | Min Module Temperature |  | int16 | C | ModTmp_SF | R | M | Minimum temperature for all modules in the bank. | Measurement.
Repeating Block |  | 43 | 15 | 1 | StrModTmpMinMod | Min Module Temperature Module |  | uint16 |  |  | R | O | Module with the miniumum temperature.
Repeating Block |  | 44 | 16 | 1 | StrModTmpAvg | Average Module Temperature |  | int16 | C | ModTmp_SF | R | M | Average temperature for all modules in the bank. | Calculation based on measurements.
Repeating Block |  | 45 | 17 | 1 | StrDisRsn | Disabled Reason |  | enum16 |  |  | R | O | Reason why the string is currently disabled.
Repeating Block |  | 46 | 18 | 2 | StrConSt | Contactor Status |  | bitfield32 |  |  | R | O | Status of the contactor(s) for the string.
Repeating Block |  | 48 | 20 | 2 | StrEvt1 | String Event 1 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Repeating Block |  | 50 | 22 | 2 | StrEvt2 | String Event 2 |  | bitfield32 |  |  | R | O | Alarms, warnings and status values. Bit flags. | Reserved for future use.
Repeating Block |  | 52 | 24 | 2 | StrEvtVnd1 | Vendor String Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events.
Repeating Block |  | 54 | 26 | 2 | StrEvtVnd2 | Vendor String Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events.
Repeating Block |  | 56 | 28 | 1 | StrSetEna | Enable/Disable String |  | enum16 |  |  | RW | O | Enables and disables the string. | Should reset to 0 upon completion.
Repeating Block |  | 57 | 29 | 1 | StrSetCon | Connect/Disconnect String |  | enum16 |  |  | RW | O | Connects and disconnects the string. | Should reset to 0 upon completion.
Repeating Block |  | 58 | 30 | 1 | Pad1 | Pad |  | pad |  |  | R | M | Pad register.
Repeating Block |  | 59 | 31 | 1 | Pad2 | Pad |  | pad |  |  | R | M | Pad register.
bitfield32 | StrSt |  |  | Name: STRING_ENABLED; Label: String Is Enabled; Value: 0 |  | String is enabled and will connect next time battery is asked to connect.
bitfield32 | StrSt |  |  | Name: CONTACTOR_STATUS; Label: Contactor Status; Value: 1 |  | String contactor is closed. | If string has multiple contactors, indicates that all contactors are closed.
enum16 | StrConFail |  |  | Name: NO_FAILURE; Label: No Failure; Value: 0 |  | Connect did not fail.
enum16 | StrConFail |  |  | Name: BUTTON_PUSHED; Label: Button Pushed; Value: 1 |  | A button was pushed which prevented connection.
enum16 | StrConFail |  |  | Name: STR_GROUND_FAULT; Label: Ground Fault; Value: 2 |  | Ground fault during auto-connect.
enum16 | StrConFail |  |  | Name: OUTSIDE_VOLTAGE_RANGE; Label: Outside Voltage Range; Value: 3 |  | Outside voltage target window during auto-connect.
enum16 | StrConFail |  |  | Name: STRING_NOT_ENABLED; Label: String Not Enabled; Value: 4 |  | The string is not enabled.
enum16 | StrConFail |  |  | Name: FUSE_OPEN; Label: Fuse Open; Value: 5 |  | A fuse is open which prevents connection.
enum16 | StrConFail |  |  | Name: CONTACTOR_FAILURE; Label: Contactor Failure; Value: 6 |  | A contactor failed to operate.
enum16 | StrConFail |  |  | Name: PRECHARGE_FAILURE; Label: Precharge Failure; Value: 7 |  | A failure during precharge occurred.
enum16 | StrConFail |  |  | Name: STRING_FAULT; Label: String Fault; Value: 8 |  | A string fault has occurred. | See StrEvt1 for more information.
enum16 | StrDisRsn |  |  | Name: NONE; Label: No Reason; Value: 0 |  | No reason provided.
enum16 | StrDisRsn |  |  | Name: FAULT; Label: Fault; Value: 1 |  | A fault has occurred which caused the string to be disabled.
enum16 | StrDisRsn |  |  | Name: MAINTENANCE; Label: Maintenance; Value: 2 |  | The string has been disabled for maintenance reasons.
enum16 | StrDisRsn |  |  | Name: EXTERNAL; Label: External; Value: 3 |  | The string has been disabled by an external user or controller.
enum16 | StrDisRsn |  |  | Name: OTHER; Label: Other; Value: 4 |  | The string has been disabled for some other reason.
bitfield32 | StrConSt |  |  | Name: CONTACTOR_0; Label: Contactor 0 Closed; Value: 0
bitfield32 | StrConSt |  |  | Name: CONTACTOR_1; Label: Contactor 1 Closed; Value: 1
bitfield32 | StrConSt |  |  | Name: CONTACTOR_2; Label: Contactor 2 Closed; Value: 2
bitfield32 | StrConSt |  |  | Name: CONTACTOR_3; Label: Contactor 3 Closed; Value: 3
bitfield32 | StrConSt |  |  | Name: CONTACTOR_4; Label: Contactor 4 Closed; Value: 4
bitfield32 | StrConSt |  |  | Name: CONTACTOR_5; Label: Contactor 5 Closed; Value: 5
bitfield32 | StrConSt |  |  | Name: CONTACTOR_6; Label: Contactor 6 Closed; Value: 6
bitfield32 | StrConSt |  |  | Name: CONTACTOR_7; Label: Contactor 7 Closed; Value: 7
bitfield32 | StrConSt |  |  | Name: CONTACTOR_8; Label: Contactor 8 Closed; Value: 8
bitfield32 | StrConSt |  |  | Name: CONTACTOR_9; Label: Contactor 9 Closed; Value: 9
bitfield32 | StrConSt |  |  | Name: CONTACTOR_10; Label: Contactor 10 Closed; Value: 10
bitfield32 | StrConSt |  |  | Name: CONTACTOR_11; Label: Contactor 11 Closed; Value: 11
bitfield32 | StrConSt |  |  | Name: CONTACTOR_12; Label: Contactor 12 Closed; Value: 12
bitfield32 | StrConSt |  |  | Name: CONTACTOR_13; Label: Contactor 13 Closed; Value: 13
bitfield32 | StrConSt |  |  | Name: CONTACTOR_14; Label: Contactor 14 Closed; Value: 14
bitfield32 | StrConSt |  |  | Name: CONTACTOR_15; Label: Contactor 15 Closed; Value: 15
bitfield32 | StrConSt |  |  | Name: CONTACTOR_16; Label: Contactor 16 Closed; Value: 16
bitfield32 | StrConSt |  |  | Name: CONTACTOR_17; Label: Contactor 17 Closed; Value: 17
bitfield32 | StrConSt |  |  | Name: CONTACTOR_18; Label: Contactor 18 Closed; Value: 18
bitfield32 | StrConSt |  |  | Name: CONTACTOR_19; Label: Contactor 19 Closed; Value: 19
bitfield32 | StrConSt |  |  | Name: CONTACTOR_20; Label: Contactor 20 Closed; Value: 20
bitfield32 | StrConSt |  |  | Name: CONTACTOR_21; Label: Contactor 21 Closed; Value: 21
bitfield32 | StrConSt |  |  | Name: CONTACTOR_22; Label: Contactor 22 Closed; Value: 22
bitfield32 | StrConSt |  |  | Name: CONTACTOR_23; Label: Contactor 23 Closed; Value: 23
bitfield32 | StrConSt |  |  | Name: CONTACTOR_24; Label: Contactor 24 Closed; Value: 24
bitfield32 | StrConSt |  |  | Name: CONTACTOR_25; Label: Contactor 25 Closed; Value: 25
bitfield32 | StrConSt |  |  | Name: CONTACTOR_26; Label: Contactor 26 Closed; Value: 26
bitfield32 | StrConSt |  |  | Name: CONTACTOR_27; Label: Contactor 27 Closed; Value: 27
bitfield32 | StrConSt |  |  | Name: CONTACTOR_28; Label: Contactor 28 Closed; Value: 28
bitfield32 | StrConSt |  |  | Name: CONTACTOR_29; Label: Contactor 29 Closed; Value: 29
bitfield32 | StrConSt |  |  | Name: CONTACTOR_30; Label: Contactor 30 Closed; Value: 30
bitfield32 | StrEvt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | String is unable to communicate with battery modules.
bitfield32 | StrEvt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Battery string has exceeded maximum operating temperature
bitfield32 | StrEvt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 2 |  | Battery string is approaching maximum operating temperature.
bitfield32 | StrEvt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 3 |  | Battery string has exceeded minimum operating temperature
bitfield32 | StrEvt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Battery string is approaching minimum operating temperature.
bitfield32 | StrEvt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Battery string maximum charge current has been exceeded. | See AChaMax in model S 802.
bitfield32 | StrEvt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 6 |  | Approaching battery string maximum charge current. | See AChaMax in model S 802.
bitfield32 | StrEvt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 7 |  | Battery string maximum discharge current has been exceeded. | See ADisChaMax in model S 802.
bitfield32 | StrEvt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching battery string maximum discharge current. | See ADisChaMax in model S 802.
bitfield32 | StrEvt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Battery string voltage has exceeded maximum limit.
bitfield32 | StrEvt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 10 |  | Battery string voltage is approaching maximum limit.
bitfield32 | StrEvt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 11 |  | Battery string voltage has exceeded minimum limit.
bitfield32 | StrEvt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Battery string voltage is approaching minimum limit.
bitfield32 | StrEvt1 |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Min Alarm; Value: 13 |  | Battery string state of charge has reached or exceeded SoCMin
bitfield32 | StrEvt1 |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Min Warning; Value: 14 |  | Battery string state of charge is approaching SoCMin
bitfield32 | StrEvt1 |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Max Alarm; Value: 15 |  | Battery string state of charge has reached or exceeded SoCMax
bitfield32 | StrEvt1 |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Max Warning; Value: 16 |  | Battery string state of charge is approaching SoCMax
bitfield32 | StrEvt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 17 |  | A voltage imbalance exists between the modules in the battery string.
bitfield32 | StrEvt1 |  |  | Name: TEMPERATURE_IMBALANCE_ALARM; Label: Temperature Imbalance Alarm; Value: 18 |  | A temperature imbalance exists between the modules in the battery string.
bitfield32 | StrEvt1 |  |  | Name: TEMPERATURE_IMBALANCE_WARNING; Label: Temperature Imbalance Warning; Value: 19 |  | A temperature imbalance is developing between the modules in the battery string.
bitfield32 | StrEvt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 20 |  | A contactor failed to open or close as requested.
bitfield32 | StrEvt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 21 |  | One or more battery fans has failed.
bitfield32 | StrEvt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 22 |  | Ground fault detected.
bitfield32 | StrEvt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 23 |  | One or more doors are open.
bitfield32 | StrEvt1 |  |  | Name: RESERVED_1; Label: Reserved; Value: 24 |  | Reserved bit. | Do not implement.
bitfield32 | StrEvt1 |  |  | Name: OTHER_ALARM; Label: Other String Alarm; Value: 25 |  | A vendor specific alarm has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | StrEvt1 |  |  | Name: OTHER_WARNING; Label: Other String Warning; Value: 26 |  | A vendor specific warning has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | StrEvt1 |  |  | Name: RESERVED_2; Label: Reserved; Value: 27 |  | Reserved bit. | Do not implement.
bitfield32 | StrEvt1 |  |  | Name: CONFIGURATION_ALARM; Label: Configuation Alarm; Value: 28 |  | The battery string has been configured incorrectly and will not operate.
bitfield32 | StrEvt1 |  |  | Name: CONFIGURATION_WARNING; Label: Configuation Warning; Value: 29 |  | The battery string has been configured incorrectly and may not operate as expected.
enum16 | StrSetEna |  |  | Name: ENABLE_STRING; Label: Enable String; Value: 1 |  | Enable the string.
enum16 | StrSetEna |  |  | Name: DISABLE_STRING; Label: Disable String; Value: 2 |  | Disable the string.
enum16 | StrSetCon |  |  | Name: CONNECT_STRING; Label: Connect String; Value: 1 |  | Connect the string.
enum16 | StrSetCon |  |  | Name: DISCONNECT_STRING; Label: Disconnect String; Value: 2 |  | Disconnect the string.

## 804
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Lithium-Ion String Model | 804 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 46 + (RB Count * 16) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Idx | String Index |  | uint16 |  |  | R | M | Index of the string within the bank. | Indices are one-based.
Fixed Block |  | 3 | 1 | 1 | NMod | Module Count |  | uint16 |  |  | R | M | Count of modules in the string.
Fixed Block |  | 4 | 2 | 2 | St | String Status |  | bitfield32 |  |  | R | M | Current status of the string.
Fixed Block |  | 6 | 4 | 1 | ConFail | Connection Failure Reason |  | enum16 |  |  | R | O
Fixed Block |  | 7 | 5 | 1 | NCellBal | String Cell Balancing Count |  | uint16 |  |  | R | O | Number of cells currently being balanced in the string.
Fixed Block |  | 8 | 6 | 1 | SoC | String State of Charge |  | uint16 | % | SoC_SF | R | M | Battery string state of charge, expressed as a percentage. | Measurement.
Fixed Block |  | 9 | 7 | 1 | DoD | String Depth of Discharge |  | uint16 | % | StrDoC_SF | R | O | Depth of discharge for the string, expressed as a percentage. | Measurement.
Fixed Block |  | 10 | 8 | 2 | NCyc | String Cycle Count |  | uint32 |  |  | R | O | Number of discharge cycles executed upon the string.
Fixed Block |  | 12 | 10 | 1 | SoH | String State of Health |  | uint16 | % | SoH_SF | R | O | Battery string state of health, expressed as a percentage. | Measurement.
Fixed Block |  | 13 | 11 | 1 | A | String Current |  | int16 | A | A_SF | R | M | String current measurement. | Measurement.
Fixed Block |  | 14 | 12 | 1 | V | String Voltage |  | uint16 | V | V_SF | R | O | String voltage measurement. | Measurement.
Fixed Block |  | 15 | 13 | 1 | CellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | M | Maximum voltage for all cells in the string. | Measurement.
Fixed Block |  | 16 | 14 | 1 | CellVMaxMod | Max Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with maximum cell voltage.
Fixed Block |  | 17 | 15 | 1 | CellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | M | Minimum voltage for all cells in the string. | Measurement.
Fixed Block |  | 18 | 16 | 1 | CellVMinMod | Min Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with minimum cell voltage.
Fixed Block |  | 19 | 17 | 1 | CellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | M | Average voltage for all cells in the string. | Calculation based on measurements.
Fixed Block |  | 20 | 18 | 1 | ModTmpMax | Max Module Temperature |  | int16 | C | ModTmp_SF | R | M | Maximum temperature for all modules in the string. | Measurement.
Fixed Block |  | 21 | 19 | 1 | ModTmpMaxMod | Max Module Temperature Module |  | uint16 |  |  | R | M | Module with the maximum temperature.
Fixed Block |  | 22 | 20 | 1 | ModTmpMin | Min Module Temperature |  | int16 | C | ModTmp_SF | R | M | Minimum temperature for all modules in the string. | Measurement.
Fixed Block |  | 23 | 21 | 1 | ModTmpMinMod | Min Module Temperature Module |  | uint16 |  |  | R | M | Module with the minimum temperature.
Fixed Block |  | 24 | 22 | 1 | ModTmpAvg | Average Module Temperature |  | int16 | C | ModTmp_SF | R | M | Average temperature for all modules in the string. | Calculation based on measurements.
Fixed Block |  | 25 | 23 | 1 | Pad1 | Pad |  | pad |  |  | R | M | Pad register.
Fixed Block |  | 26 | 24 | 2 | ConSt | Contactor Status |  | bitfield32 |  |  | R | O | Status of the contactor(s) for the string.
Fixed Block |  | 28 | 26 | 2 | Evt1 | String Event 1 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Fixed Block |  | 30 | 28 | 2 | Evt2 | String Event 2 |  | bitfield32 |  |  | R | O | Alarms, warnings and status values. Bit flags. | Reserved for future use.
Fixed Block |  | 32 | 30 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | O | Vendor defined events.
Fixed Block |  | 34 | 32 | 2 | EvtVnd2 | Vendor Event Bitfield 2 |  | bitfield32 |  |  | R | O | Vendor defined events.
Fixed Block |  | 36 | 34 | 1 | SetEna | Enable/Disable String |  | enum16 |  |  | RW | O | Enables and disables the string. Should reset to 0 upon completion.
Fixed Block |  | 37 | 35 | 1 | SetCon | Connect/Disconnect String |  | enum16 |  |  | RW | O | Connects and disconnects the string. | Should reset to 0 upon completion.
Fixed Block |  | 38 | 36 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | M | Scale factor for string state of charge.
Fixed Block |  | 39 | 37 | Size: 1; Name: SoH_SF; Type: sunssf; R/W: R | O | Scale factor for string state of health.
Fixed Block |  | 40 | 38 | Size: 1; Name: DoD_SF; Type: sunssf; R/W: R | O | Scale factor for string depth of discharge.
Fixed Block |  | 41 | 39 | Size: 1; Name: A_SF; Type: sunssf; R/W: R | M | Scale factor for string current.
Fixed Block |  | 42 | 40 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | O | Scale factor for string voltage.
Fixed Block |  | 43 | 41 | Size: 1; Name: CellV_SF; Type: sunssf; R/W: R | M | Scale factor for cell voltage.
Fixed Block |  | 44 | 42 | Size: 1; Name: ModTmp_SF; Type: sunssf; R/W: R | M | Scale factor for module temperature.
Fixed Block |  | 45 | 43 | 1 | Pad2 | Pad |  | pad |  |  | R | M | Pad register.
Fixed Block |  | 46 | 44 | 1 | Pad3 | Pad |  | pad |  |  | R | M | Pad register.
Fixed Block |  | 47 | 45 | 1 | Pad4 | Pad |  | pad |  |  | R | M | Pad register.
Repeating Block |  | 48 | 0 | 1 | ModNCell | Module Cell Count |  | uint16 |  |  | R | M | Count of all cells in the module.
Repeating Block |  | 49 | 1 | 1 | ModSoC | Module SoC |  | uint16 | % | SoC_SF | R | O | Module state of charge, expressed as a percentage.
Repeating Block |  | 50 | 2 | 1 | ModSoH | Module SoH |  | uint16 | % | SoH_SF | R | O | Module state of health, expressed as a percentage.
Repeating Block |  | 51 | 3 | 1 | ModCellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | M | Maximum voltage for all cells in the module. | Measurement.
Repeating Block |  | 52 | 4 | 1 | ModCellVMaxCell | Max Cell Voltage Cell |  | uint16 |  |  | R | O | Cell with maximum voltage.
Repeating Block |  | 53 | 5 | 1 | ModCellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | M | Minimum voltage for all cells in the module. | Measurement.
Repeating Block |  | 54 | 6 | 1 | ModCellVMinCell | Min Cell Voltage Cell |  | uint16 | V | CellV_SF | R | O | Cell with minimum voltage.
Repeating Block |  | 55 | 7 | 1 | ModCellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | M | Average voltage for all cells in the module. | Calculation based on measurements.
Repeating Block |  | 56 | 8 | 1 | ModCellTmpMax | Max Cell Temperature |  | int16 | C | ModTmp_SF | R | M | Maximum temperature for all cells in the module. | Measurement.
Repeating Block |  | 57 | 9 | 1 | ModCellTmpMaxCell | Max Cell Temperature Cell |  | uint16 |  |  | R | O | Cell with maximum temperature.
Repeating Block |  | 58 | 10 | 1 | ModCellTmpMin | Min Cell Temperature |  | int16 | C | ModTmp_SF | R | M | Minimum temperature for all cells in the module. | Measurement.
Repeating Block |  | 59 | 11 | 1 | ModCellTmpMinCell | Min Cell Temperature Cell |  | uint16 |  |  | R | O | Cell with minimum temperature.
Repeating Block |  | 60 | 12 | 1 | ModCellTmpAvg | Average Cell Temperature |  | int16 | C | ModTmp_SF | R | M | Average temperature for all cells in the module. | Calculation based on measurements.
Repeating Block |  | 61 | 13 | 1 | Pad5 | Pad |  | pad |  |  | R | M | Pad register.
Repeating Block |  | 62 | 14 | 1 | Pad6 | Pad |  | pad |  |  | R | M | Pad register.
Repeating Block |  | 63 | 15 | 1 | Pad7 | Pad |  | pad |  |  | R | M | Pad register.
bitfield32 | St |  |  | Name: STRING_ENABLED; Label: String Is Enabled; Value: 0 |  | String is enabled and will connect next time battery is asked to connect.
bitfield32 | St |  |  | Name: CONTACTOR_STATUS; Label: Contactor Status; Value: 1 |  | String contactor is closed. | If string has multiple contactors, indicates that all contactors are closed.
enum16 | ConFail |  |  | Name: NO_FAILURE; Label: No Failure; Value: 0 |  | Connect did not fail.
enum16 | ConFail |  |  | Name: BUTTON_PUSHED; Label: Button Pushed; Value: 1 |  | A button was pushed which prevented connection.
enum16 | ConFail |  |  | Name: STR_GROUND_FAULT; Label: Ground Fault; Value: 2 |  | Ground fault during auto-connect.
enum16 | ConFail |  |  | Name: OUTSIDE_VOLTAGE_RANGE; Label: Outside Voltage Range; Value: 3 |  | Outside voltage target window during auto-connect.
enum16 | ConFail |  |  | Name: STRING_NOT_ENABLED; Label: String Not Enabled; Value: 4 |  | The string is not enabled.
enum16 | ConFail |  |  | Name: FUSE_OPEN; Label: Fuse Open; Value: 5 |  | A fuse is open which prevents connection.
enum16 | ConFail |  |  | Name: CONTACTOR_FAILURE; Label: Contactor Failure; Value: 6 |  | A contactor failed to operate.
enum16 | ConFail |  |  | Name: PRECHARGE_FAILURE; Label: Precharge Failure; Value: 7 |  | A precharge failure occurred.
enum16 | ConFail |  |  | Name: STRING_FAULT; Label: String Fault; Value: 8 |  | A string fault has occurred. | See Evt1 for more information.
bitfield32 | ConSt |  |  | Name: CONTACTOR_0; Label: Contactor 0 Closed; Value: 0
bitfield32 | ConSt |  |  | Name: CONTACTOR_1; Label: Contactor 1 Closed; Value: 1
bitfield32 | ConSt |  |  | Name: CONTACTOR_2; Label: Contactor 2 Closed; Value: 2
bitfield32 | ConSt |  |  | Name: CONTACTOR_3; Label: Contactor 3 Closed; Value: 3
bitfield32 | ConSt |  |  | Name: CONTACTOR_4; Label: Contactor 4 Closed; Value: 4
bitfield32 | ConSt |  |  | Name: CONTACTOR_5; Label: Contactor 5 Closed; Value: 5
bitfield32 | ConSt |  |  | Name: CONTACTOR_6; Label: Contactor 6 Closed; Value: 6
bitfield32 | ConSt |  |  | Name: CONTACTOR_7; Label: Contactor 7 Closed; Value: 7
bitfield32 | ConSt |  |  | Name: CONTACTOR_8; Label: Contactor 8 Closed; Value: 8
bitfield32 | ConSt |  |  | Name: CONTACTOR_9; Label: Contactor 9 Closed; Value: 9
bitfield32 | ConSt |  |  | Name: CONTACTOR_10; Label: Contactor 10 Closed; Value: 10
bitfield32 | ConSt |  |  | Name: CONTACTOR_11; Label: Contactor 11 Closed; Value: 11
bitfield32 | ConSt |  |  | Name: CONTACTOR_12; Label: Contactor 12 Closed; Value: 12
bitfield32 | ConSt |  |  | Name: CONTACTOR_13; Label: Contactor 13 Closed; Value: 13
bitfield32 | ConSt |  |  | Name: CONTACTOR_14; Label: Contactor 14 Closed; Value: 14
bitfield32 | ConSt |  |  | Name: CONTACTOR_15; Label: Contactor 15 Closed; Value: 15
bitfield32 | ConSt |  |  | Name: CONTACTOR_16; Label: Contactor 16 Closed; Value: 16
bitfield32 | ConSt |  |  | Name: CONTACTOR_17; Label: Contactor 17 Closed; Value: 17
bitfield32 | ConSt |  |  | Name: CONTACTOR_18; Label: Contactor 18 Closed; Value: 18
bitfield32 | ConSt |  |  | Name: CONTACTOR_19; Label: Contactor 19 Closed; Value: 19
bitfield32 | ConSt |  |  | Name: CONTACTOR_20; Label: Contactor 20 Closed; Value: 20
bitfield32 | ConSt |  |  | Name: CONTACTOR_21; Label: Contactor 21 Closed; Value: 21
bitfield32 | ConSt |  |  | Name: CONTACTOR_22; Label: Contactor 22 Closed; Value: 22
bitfield32 | ConSt |  |  | Name: CONTACTOR_23; Label: Contactor 23 Closed; Value: 23
bitfield32 | ConSt |  |  | Name: CONTACTOR_24; Label: Contactor 24 Closed; Value: 24
bitfield32 | ConSt |  |  | Name: CONTACTOR_25; Label: Contactor 25 Closed; Value: 25
bitfield32 | ConSt |  |  | Name: CONTACTOR_26; Label: Contactor 26 Closed; Value: 26
bitfield32 | ConSt |  |  | Name: CONTACTOR_27; Label: Contactor 27 Closed; Value: 27
bitfield32 | ConSt |  |  | Name: CONTACTOR_28; Label: Contactor 28 Closed; Value: 28
bitfield32 | ConSt |  |  | Name: CONTACTOR_29; Label: Contactor 29 Closed; Value: 29
bitfield32 | ConSt |  |  | Name: CONTACTOR_30; Label: Contactor 30 Closed; Value: 30
bitfield32 | Evt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | String is unable to communicate with battery modules.
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Battery string has exceeded maximum operating temperature
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 2 |  | Battery string is approaching maximum operating temperature.
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 3 |  | Battery string has exceeded minimum operating temperature
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Battery string is approaching minimum operating temperature.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Battery string maximum charge current has been exceeded. | See AChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 6 |  | Approaching battery string maximum charge current. | See AChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 7 |  | Battery string maximum discharge current has been exceeded. | See ADisChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching battery string maximum discharge current. | See ADisChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Battery string voltage has exceeded maximum limit.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 10 |  | Battery string voltage is approaching maximum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 11 |  | Battery string voltage has exceeded minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Battery string voltage is approaching minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Min Alarm; Value: 13 |  | Battery string state of charge has reached or exceeded SoCMin.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Min Warning; Value: 14 |  | Battery string state of charge is approaching SoCMin.
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Max Alarm; Value: 15 |  | Battery string state of charge has reached or exceeded SoCMax.
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Max Warning; Value: 16 |  | Battery string state of charge is approaching SoCMax.
bitfield32 | Evt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 17 |  | A voltage imbalance exists between the modules in the battery string.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_ALARM; Label: Temperature Imbalance Alarm; Value: 18 |  | A temperature imbalance exists between the modules in the battery string.
bitfield32 | Evt1 |  |  | Name: TEMPERATURE_IMBALANCE_WARNING; Label: Temperature Imbalance Warning; Value: 19 |  | A temperature imbalance is developing between the modules in the battery string.
bitfield32 | Evt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 20 |  | A contactor failed to open or close as requested.
bitfield32 | Evt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 21 |  | One or more battery fans has failed.
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 22 |  | Ground fault detected.
bitfield32 | Evt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 23 |  | One or more doors are open.
bitfield32 | Evt1 |  |  | Name: RESERVED_1; Label: Reserved; Value: 24 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: OTHER_ALARM; Label: Other String Alarm; Value: 25 |  | A vendor specific alarm has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: OTHER_WARNING; Label: Other String Warning; Value: 26 |  | A vendor specific warning has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: RESERVED_2; Label: Reserved; Value: 27 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_ALARM; Label: Configuation Alarm; Value: 28 |  | The battery string has been configured incorrectly and will not operate as expected.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_WARNING; Label: Configuation Warning; Value: 29 |  | The battery string has been configured incorrectly and may not operate as expected.
enum16 | SetCon |  |  | Name: CONNECT_STRING; Label: Connect String; Value: 1 |  | Connect the string.
enum16 | SetCon |  |  | Name: DISCONNECT_STRING; Label: Disconnect String; Value: 2 |  | Disconnect the string.

## 805
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Lithium-Ion Module Model | 805 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 42 + (RB Count * 4) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | StrIdx | String Index |  | uint16 |  |  | R | M | Index of the string containing the module. | Indices are one-based.
Fixed Block |  | 3 | 1 | 1 | ModIdx | Module Index |  | uint16 |  |  | R | M | Index of the module within the string. | Indices are one-based.
Fixed Block |  | 4 | 2 | 1 | NCell | Module Cell Count |  | uint16 |  |  | R | M | Count of all cells in the module.
Fixed Block |  | 5 | 3 | 1 | SoC | Module SoC |  | uint16 | % | SoC_SF | R | O | Module state of charge, expressed as a percentage.
Fixed Block |  | 6 | 4 | 1 | DoD | Depth of Discharge |  | uint16 | % | DoD_SF | R | O | Depth ofdischarge for the module. | Measurement.
Fixed Block |  | 7 | 5 | 1 | SoH | Module SoH |  | uint16 | % | SoH_SF | R | O | Module state of health, expressed as a percentage.
Fixed Block |  | 8 | 6 | 2 | NCyc | Cycle Count |  | uint32 |  |  | R | O | Count of cycles executed.
Fixed Block |  | 10 | 8 | 1 | V | Module Voltage |  | uint16 | V | V_SF | R | M | Voltage of the module. | Measurement.
Fixed Block |  | 11 | 9 | 1 | CellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | M | Maximum voltage for all cells in the module. | Measurement.
Fixed Block |  | 12 | 10 | 1 | CellVMaxCell | Max Cell Voltage Cell |  | uint16 |  |  | R | O | Cell with the maximum voltage.
Fixed Block |  | 13 | 11 | 1 | CellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | M | Minimum voltage for all cells in the module. | Measurement.
Fixed Block |  | 14 | 12 | 1 | CellVMinCell | Min Cell Voltage Cell |  | uint16 |  |  | R | O | Cell with the minimum voltage.
Fixed Block |  | 15 | 13 | 1 | CellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | M | Average voltage for all cells in the module. | Calculation based on measurements.
Fixed Block |  | 16 | 14 | 1 | CellTmpMax | Max Cell Temperature |  | int16 | C | Tmp_SF | R | M | Maximum temperature for all cells in the module. | Measurement.
Fixed Block |  | 17 | 15 | 1 | CellTmpMaxCell | Max Cell Temperature Cell |  | uint16 |  |  | R | O | Cell with the maximum cell temperature.
Fixed Block |  | 18 | 16 | 1 | CellTmpMin | Min Cell Temperature |  | int16 | C | Tmp_SF | R | M | Minimum temperature for all cells in the module. | Measurement.
Fixed Block |  | 19 | 17 | 1 | CellTmpMinCell | Max Cell Temperature Cell |  | uint16 |  |  | R | O | Cell with the maximum cell temperature.
Fixed Block |  | 20 | 18 | 1 | CellTmpAvg | Average Cell Temperature |  | int16 | C | Tmp_SF | R | M | Average temperature for all cells in the module. | Calculation based on measurements.
Fixed Block |  | 21 | 19 | 1 | NCellBal | Balanced Cell Count |  | uint16 |  |  | R | O | Number of cells currently being balanced in the module.
Fixed Block |  | 22 | 20 | 16 | SN | Serial Number |  | string |  |  | R | O | Serial number for the module.
Fixed Block |  | 38 | 36 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | O | Scale factor for module state of charge.
Fixed Block |  | 39 | 37 | Size: 1; Name: SoH_SF; Type: sunssf; R/W: R | O | Scale factor for module state of health.
Fixed Block |  | 40 | 38 | Size: 1; Name: DoD_SF; Type: sunssf; R/W: R | O | Scale factor for module depth of discharge.
Fixed Block |  | 41 | 39 | Size: 1; Name: V_SF; Type: sunssf; R/W: R | M | Scale factor for module voltage.
Fixed Block |  | 42 | 40 | Size: 1; Name: CellV_SF; Type: sunssf; R/W: R | M | Scale factor for cell voltage.
Fixed Block |  | 43 | 41 | Size: 1; Name: Tmp_SF; Type: sunssf; R/W: R | M | Scale factor for module temperature.
Repeating Block |  | 44 | 0 | 1 | CellV | Cell Voltage |  | uint16 | V | CellV_SF | R | M | Cell terminal voltage. | Measurement.
Repeating Block |  | 45 | 1 | 1 | CellTmp | Cell Temperature |  | int16 | C | Tmp_SF | R | M | Cell temperature. | Measurement.
Repeating Block |  | 46 | 2 | 2 | CellSt | Cell Status |  | bitfield32 |  |  | R | O | Status of the cell.
bitfield32 | CellSt |  |  | Name: CELL_IS_BALANCING; Label: Cell Is Balancing; Value: 0 |  | Cell is currently being balanced.

## 806
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Flow Battery Model | 806 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 1 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | BatTBD | Battery Points To Be Determined |  | uint16 |  |  | R | M
Repeating Block |  | 3 | 0 | 1 | BatStTBD | Battery String Points To Be Determined |  | uint16 |  |  | R | M

## 807
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Flow Battery String Model | 807 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 34 + (RB Count * 24) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | Idx | String Index |  | uint16 |  |  | R | M | Index of the string within the bank. | Indices are one-based.
Fixed Block |  | 3 | 1 | 1 | NMod | Module Count |  | uint16 |  |  | R | M | Number of modules in this string.
Fixed Block |  | 4 | 2 | 1 | NModCon | Connected Module Count |  | uint16 |  |  | R | M | Number of electrically connected modules in this string.
Fixed Block |  | 5 | 3 | 1 | ModVMax | Max Module Voltage |  | uint16 | V | ModV_SF | R | M | Maximum voltage for all modules in the string. | Measurement.
Fixed Block |  | 6 | 4 | 1 | ModVMaxMod | Max Module Voltage Module |  | uint16 |  |  | R | O | Module with the maximum voltage.
Fixed Block |  | 7 | 5 | 1 | ModVMin | Min Module Voltage |  | uint16 | V | ModV_SF | R | M | Minimum voltage for all modules in the string. | Measurement.
Fixed Block |  | 8 | 6 | 1 | ModVMinMod | Min Module Voltage Module |  | uint16 |  |  | R | O | Module with the minimum voltage.
Fixed Block |  | 9 | 7 | 1 | ModVAvg | Average Module Voltage |  | uint16 | V | ModV_SF | R | M | Average voltage for all modules in the string. | Calculation based on measurements.
Fixed Block |  | 10 | 8 | 1 | CellVMax | Max Cell Voltage |  | uint16 | V | CellV_SF | R | O | Maximum voltage for all cells in the string. | Measurement.
Fixed Block |  | 11 | 9 | 1 | CellVMaxMod | Max Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with the maximum voltage.
Fixed Block |  | 12 | 10 | 1 | CellVMaxStk | Max Cell Voltage Stack |  | uint16 |  |  | R | O | Stack containing the cell with the maximum voltage.
Fixed Block |  | 13 | 11 | 1 | CellVMin | Min Cell Voltage |  | uint16 | V | CellV_SF | R | O | Minimum voltage for all cells in the string. | Measurement.
Fixed Block |  | 14 | 12 | 1 | CellVMinMod | Min Cell Voltage Module |  | uint16 |  |  | R | O | Module containing the cell with the minimum voltage.
Fixed Block |  | 15 | 13 | 1 | CellVMinStk | Min Cell Voltage Stack |  | uint16 |  |  | R | O | Stack containing the cell with the minimum voltage.
Fixed Block |  | 16 | 14 | 1 | CellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | O | Average voltage for all cells in the string. | Calculation based on measurements.
Fixed Block |  | 17 | 15 | 1 | TmpMax | Max Temperature |  | int16 | C | Tmp_SF | R | M | Maximum electrolyte temperature for all modules in the string. | Measurement.
Fixed Block |  | 18 | 16 | 1 | TmpMaxMod | Max Temperature Module |  | uint16 |  |  | R | O | Module with the maximum temperature.
Fixed Block |  | 19 | 17 | 1 | TmpMin | Min Temperature |  | int16 | C | Tmp_SF | R | M | Minimum electrolyte temperature for all modules in the string. | Measurement.
Fixed Block |  | 20 | 18 | 1 | TmpMinMod | Min Temperature Module |  | uint16 |  |  | R | O | Module with the minimum temperature.
Fixed Block |  | 21 | 19 | 1 | TmpAvg | Average Temperature |  | int16 | C | Tmp_SF | R | M | Average electrolyte temperature for all modules in the string. | Calculation based on measurements.
Fixed Block |  | 22 | 20 | 2 | Evt1 | String Event 1 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Fixed Block |  | 24 | 22 | 2 | Evt2 | String Event 2 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Fixed Block |  | 26 | 24 | 2 | EvtVnd1 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | M | Vendor defined events.
Fixed Block |  | 28 | 26 | 2 | EvtVnd2 | Vendor Event Bitfield 1 |  | bitfield32 |  |  | R | M | Vendor defined events.
Fixed Block |  | 30 | 28 | Size: 1; Name: ModV_SF; Type: sunssf; R/W: R | M
Fixed Block |  | 31 | 29 | Size: 1; Name: CellV_SF; Type: sunssf; R/W: R | M | Scale factor for voltage.
Fixed Block |  | 32 | 30 | Size: 1; Name: Tmp_SF; Type: sunssf; R/W: R | M | Scale factor for temperature.
Fixed Block |  | 33 | 31 | Size: 1; Name: SoC_SF; Type: sunssf; R/W: R | M | Scale factor for state of charge.
Fixed Block |  | 34 | 32 | Size: 1; Name: OCV_SF; Type: sunssf; R/W: R | M | Scale factor for open circuit voltage.
Fixed Block |  | 35 | 33 | 1 | Pad1 | Pad |  | pad |  |  | R | M | Pad register.
Repeating Block |  | 36 | 0 | 1 | ModIdx | Module Index |  | uint16 |  |  | R | M | Index of the module within the string. | Indices are one-based.
Repeating Block |  | 37 | 1 | 1 | ModNStk | Stack Count |  | uint16 |  |  | R | M | Number of stacks in this module.
Repeating Block |  | 38 | 2 | 2 | ModSt | Module Status |  | bitfield32 |  |  | R | M | Current status of the module.
Repeating Block |  | 40 | 4 | 1 | ModSoC | Module State of Charge |  | uint16 | % | SoC_SF | R | M | State of charge for this module.
Repeating Block |  | 41 | 5 | 1 | ModOCV | Open Circuit Voltage |  | uint16 | V | OCV_SF | R | M | Open circuit voltage for this module.
Repeating Block |  | 42 | 6 | 1 | ModV | External Voltage |  | uint16 | V | ModV_SF | R | M | External voltage fo this module.
Repeating Block |  | 43 | 7 | 1 | ModCellVMax | Maximum Cell Voltage |  | uint16 | V | CellV_SF | R | O | Maximum voltage for all cells in this module. | Measurement.
Repeating Block |  | 44 | 8 | 1 | ModCellVMaxCell | Max Cell Voltage Cell |  | uint16 |  |  | R | O | Cell with the maximum cell voltage.
Repeating Block |  | 45 | 9 | 1 | ModCellVMin | Minimum Cell Voltage |  | uint16 | V | CellV_SF | R | O | Minimum voltage for all cells in this module. | Measurement.
Repeating Block |  | 46 | 10 | 1 | ModCellVMinCell | Min Cell Voltage Cell |  | uint16 |  |  | R | O | Cell with the minimum cell voltage.
Repeating Block |  | 47 | 11 | 1 | ModCellVAvg | Average Cell Voltage |  | uint16 | V | CellV_SF | R | O | Average voltage for all cells in this module. | Calculation based on measurements.
Repeating Block |  | 48 | 12 | 1 | ModAnoTmp | Anolyte Temperature |  | uint16 | C | Tmp_SF | R | O
Repeating Block |  | 49 | 13 | 1 | ModCatTmp | Catholyte Temperature |  | uint16 | C | Tmp_SF | R | O
Repeating Block |  | 50 | 14 | 2 | ModConSt | Contactor Status |  | bitfield32 |  |  | R | O
Repeating Block |  | 52 | 16 | 2 | ModEvt1 | Module Event 1 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Repeating Block |  | 54 | 18 | 2 | ModEvt2 | Module Event 2 |  | bitfield32 |  |  | R | M | Alarms, warnings and status values. Bit flags.
Repeating Block |  | 56 | 20 | 1 | ModConFail | Connection Failure Reason |  | enum16 |  |  | R | O
Repeating Block |  | 57 | 21 | 1 | ModSetEna | Enable/Disable Module |  | enum16 |  |  | RW | O | Enables and disables the module. | Should reset to 0 upon completion.
Repeating Block |  | 58 | 22 | 1 | ModSetCon | Connect/Disconnect Module |  | enum16 |  |  | RW | O | Connects and disconnects the module. | Should reset to 0 upon completion.
Repeating Block |  | 59 | 23 | 1 | ModDisRsn | Disabled Reason |  | enum16 |  |  | R | O | Reason why the module is currently disabled.
bitfield32 | Evt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | Module is unable to communicate with the BMS or other components.
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Module has exceeded maximum operating temperature
bitfield32 | Evt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 2 |  | Module is approaching maximum operating temperature.
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 3 |  | Module has exceeded minimum operating temperature
bitfield32 | Evt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Module is approaching minimum operating temperature.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Module maximum charge current has been exceeded. | See AChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 6 |  | Approaching module maximum charge current. | See AChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 7 |  | Module maximum discharge current has been exceeded. | See ADisChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching module maximum discharge current. | See ADisChaMax in model S 802.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Module voltage has exceeded maximum limit.
bitfield32 | Evt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 10 |  | Module voltage is approaching maximum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 11 |  | Module voltage has exceeded minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Module voltage is approaching minimum limit.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Minimum Alarm; Value: 13 |  | Module state of charge has reached or exceeded SoCMin.
bitfield32 | Evt1 |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Minimum Warning; Value: 14 |  | Module state of charge is approaching SoCMin.
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Maximum Alarm; Value: 15 |  | Module state of charge has reached or exceeded SoCMax.
bitfield32 | Evt1 |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Maximum Warning; Value: 16 |  | Module state of charge is approaching SoCMax.
bitfield32 | Evt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 17 |  | A voltage imbalance exists between the stacks in the module.
bitfield32 | Evt1 |  |  | Name: RESERVED_1; Label: Reserved; Value: 18 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: RESERVED_2; Label: Reserved; Value: 19 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 20 |  | A contactor failed to open or close as requested.
bitfield32 | Evt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 21 |  | One or more module fans has failed.
bitfield32 | Evt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 22 |  | Ground fault detected.
bitfield32 | Evt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 23 |  | One or more doors are open.
bitfield32 | Evt1 |  |  | Name: RESERVED_3; Label: Reserved; Value: 24 |  | Reserved bit. | Do not implement.
bitfield32 | Evt1 |  |  | Name: OTHER_ALARM; Label: Other String Alarm; Value: 25 |  | A vendor specific alarm has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: OTHER_WARNING; Label: Other String Warning; Value: 26 |  | A vendor specific warning has occurred. | See EvtVnd1 and EvtVnd2 for more information.
bitfield32 | Evt1 |  |  | Name: FIRE_ALARM; Label: Fire Alarm; Value: 27 |  | A fire has been detected.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_ALARM; Label: Configuation Alarm; Value: 28 |  | The battery string has been configured incorrectly and will not operate.
bitfield32 | Evt1 |  |  | Name: CONFIGURATION_WARNING; Label: Configuation Warning; Value: 29 |  | The battery string has been configured incorrectly and may not operate as expected.
bitfield32 | Evt2 |  |  | Name: LEAK_ALARM; Label: Leak Alarm; Value: 0 |  | A leak has been detected.
bitfield32 | Evt2 |  |  | Name: PUMP_ALARM; Label: Pump Alarm; Value: 1 |  | A pump has experienced an alarm condition or some other error.
bitfield32 | Evt2 |  |  | Name: HIGH_PRESSURE_ALARM; Label: High Pressure Alarm; Value: 2 |  | Pressure exceeds maximum value.
bitfield32 | Evt2 |  |  | Name: HIGH_PRESSURE_WARNING; Label: High Pressure Warning; Value: 3 |  | Pressure approaching maximum value.
bitfield32 | Evt2 |  |  | Name: LOW_FLOW_ALARM; Label: Low Flow Alarm; Value: 4 |  | Flow exceeds minimum value.
bitfield32 | Evt2 |  |  | Name: LOW_FLOW_WARNING; Label: Low Flow Warning; Value: 5 |  | Flow approaching minimum value.
bitfield32 | ModSt |  |  | Name: MODULE_ENABLED; Label: Module Is Enabled; Value: 0 |  | Module is enabled and will connect next time battery is asked to connect.
bitfield32 | ModSt |  |  | Name: CONTACTOR_STATUS; Label: Contactor Status; Value: 1 |  | Module contactor is closed. | If module has multiple contactors, indicates that all contactors are closed.
bitfield32 | ModConSt |  |  | Name: CONTACTOR_0; Label: Contactor 0 Closed; Value: 0
bitfield32 | ModConSt |  |  | Name: CONTACTOR_1; Label: Contactor 1 Closed; Value: 1
bitfield32 | ModConSt |  |  | Name: CONTACTOR_2; Label: Contactor 2 Closed; Value: 2
bitfield32 | ModConSt |  |  | Name: CONTACTOR_3; Label: Contactor 3 Closed; Value: 3
bitfield32 | ModConSt |  |  | Name: CONTACTOR_4; Label: Contactor 4 Closed; Value: 4
bitfield32 | ModConSt |  |  | Name: CONTACTOR_5; Label: Contactor 5 Closed; Value: 5
bitfield32 | ModConSt |  |  | Name: CONTACTOR_6; Label: Contactor 6 Closed; Value: 6
bitfield32 | ModConSt |  |  | Name: CONTACTOR_7; Label: Contactor 7 Closed; Value: 7
bitfield32 | ModConSt |  |  | Name: CONTACTOR_8; Label: Contactor 8 Closed; Value: 8
bitfield32 | ModConSt |  |  | Name: CONTACTOR_9; Label: Contactor 9 Closed; Value: 9
bitfield32 | ModConSt |  |  | Name: CONTACTOR_10; Label: Contactor 10 Closed; Value: 10
bitfield32 | ModConSt |  |  | Name: CONTACTOR_11; Label: Contactor 11 Closed; Value: 11
bitfield32 | ModConSt |  |  | Name: CONTACTOR_12; Label: Contactor 12 Closed; Value: 12
bitfield32 | ModConSt |  |  | Name: CONTACTOR_13; Label: Contactor 13 Closed; Value: 13
bitfield32 | ModConSt |  |  | Name: CONTACTOR_14; Label: Contactor 14 Closed; Value: 14
bitfield32 | ModConSt |  |  | Name: CONTACTOR_15; Label: Contactor 15 Closed; Value: 15
bitfield32 | ModConSt |  |  | Name: CONTACTOR_16; Label: Contactor 16 Closed; Value: 16
bitfield32 | ModConSt |  |  | Name: CONTACTOR_17; Label: Contactor 17 Closed; Value: 17
bitfield32 | ModConSt |  |  | Name: CONTACTOR_18; Label: Contactor 18 Closed; Value: 18
bitfield32 | ModConSt |  |  | Name: CONTACTOR_19; Label: Contactor 19 Closed; Value: 19
bitfield32 | ModConSt |  |  | Name: CONTACTOR_20; Label: Contactor 20 Closed; Value: 20
bitfield32 | ModConSt |  |  | Name: CONTACTOR_21; Label: Contactor 21 Closed; Value: 21
bitfield32 | ModConSt |  |  | Name: CONTACTOR_22; Label: Contactor 22 Closed; Value: 22
bitfield32 | ModConSt |  |  | Name: CONTACTOR_23; Label: Contactor 23 Closed; Value: 23
bitfield32 | ModConSt |  |  | Name: CONTACTOR_24; Label: Contactor 24 Closed; Value: 24
bitfield32 | ModConSt |  |  | Name: CONTACTOR_25; Label: Contactor 25 Closed; Value: 25
bitfield32 | ModConSt |  |  | Name: CONTACTOR_26; Label: Contactor 26 Closed; Value: 26
bitfield32 | ModConSt |  |  | Name: CONTACTOR_27; Label: Contactor 27 Closed; Value: 27
bitfield32 | ModConSt |  |  | Name: CONTACTOR_28; Label: Contactor 28 Closed; Value: 28
bitfield32 | ModConSt |  |  | Name: CONTACTOR_29; Label: Contactor 29 Closed; Value: 29
bitfield32 | ModConSt |  |  | Name: CONTACTOR_30; Label: Contactor 30 Closed; Value: 30
bitfield32 | ModEvt1 |  |  | Name: COMMUNICATION_ERROR; Label: Communication Error; Value: 0 |  | Module is unable to communicate with the BMS or other components.
bitfield32 | ModEvt1 |  |  | Name: OVER_TEMP_ALARM; Label: Over Temperature Alarm; Value: 1 |  | Module has exceeded maximum operating temperature
bitfield32 | ModEvt1 |  |  | Name: OVER_TEMP_WARNING; Label: Over Temperature Warning; Value: 2 |  | Module is approaching maximum operating temperature.
bitfield32 | ModEvt1 |  |  | Name: UNDER_TEMP_ALARM; Label: Under Temperature Alarm; Value: 3 |  | Module has exceeded minimum operating temperature
bitfield32 | ModEvt1 |  |  | Name: UNDER_TEMP_WARNING; Label: Under Temperature Warning; Value: 4 |  | Module is approaching minimum operating temperature.
bitfield32 | ModEvt1 |  |  | Name: OVER_CHARGE_CURRENT_ALARM; Label: Over Charge Current Alarm; Value: 5 |  | Module maximum charge current has been exceeded. | See AChaMax in model S 802.
bitfield32 | ModEvt1 |  |  | Name: OVER_CHARGE_CURRENT_WARNING; Label: Over Charge Current Warning; Value: 6 |  | Approaching module maximum charge current. | See AChaMax in model S 802.
bitfield32 | ModEvt1 |  |  | Name: OVER_DISCHARGE_CURRENT_ALARM; Label: Over Discharge Current Alarm; Value: 7 |  | Module maximum discharge current has been exceeded. | See ADisChaMax in model S 802.
bitfield32 | ModEvt1 |  |  | Name: OVER_DISCHARGE_CURRENT_WARNING; Label: Over Discharge Current Warning; Value: 8 |  | Approaching module maximum discharge current. | See ADisChaMax in model S 802.
bitfield32 | ModEvt1 |  |  | Name: OVER_VOLT_ALARM; Label: Over Voltage Alarm; Value: 9 |  | Module voltage has exceeded maximum limit.
bitfield32 | ModEvt1 |  |  | Name: OVER_VOLT_WARNING; Label: Over Voltage Warning; Value: 10 |  | Module voltage is approaching maximum limit.
bitfield32 | ModEvt1 |  |  | Name: UNDER_VOLT_ALARM; Label: Under Voltage Alarm; Value: 11 |  | Module voltage has exceeded minimum limit.
bitfield32 | ModEvt1 |  |  | Name: UNDER_VOLT_WARNING; Label: Under Voltage Warning; Value: 12 |  | Module voltage is approaching minimum limit.
bitfield32 | ModEvt1 |  |  | Name: UNDER_SOC_MIN_ALARM; Label: Under State of Charge Minimum Alarm; Value: 13 |  | Module state of charge has reached or exceeded SoCMin.
bitfield32 | ModEvt1 |  |  | Name: UNDER_SOC_MIN_WARNING; Label: Under State of Charge Minimum Warning; Value: 14 |  | Module state of charge is approaching SoCMin.
bitfield32 | ModEvt1 |  |  | Name: OVER_SOC_MAX_ALARM; Label: Over State of Charge Maximum Alarm; Value: 15 |  | Module state of charge has reached or exceeded SoCMax.
bitfield32 | ModEvt1 |  |  | Name: OVER_SOC_MAX_WARNING; Label: Over State of Charge Maximum Warning; Value: 16 |  | Module state of charge is approaching SoCMax.
bitfield32 | ModEvt1 |  |  | Name: VOLTAGE_IMBALANCE_WARNING; Label: Voltage Imbalance Warning; Value: 17 |  | A voltage imbalance exists between the stacks in the module.
bitfield32 | ModEvt1 |  |  | Name: RESERVED_1; Label: Reserved; Value: 18 |  | Reserved bit. | Do not implement.
bitfield32 | ModEvt1 |  |  | Name: RESERVED_2; Label: Reserved; Value: 19 |  | Reserved bit. | Do not implement.
bitfield32 | ModEvt1 |  |  | Name: CONTACTOR_ERROR; Label: Contactor Error; Value: 20 |  | A contactor failed to open or close as requested.
bitfield32 | ModEvt1 |  |  | Name: FAN_ERROR; Label: Fan Error; Value: 21 |  | One or more module fans has failed.
bitfield32 | ModEvt1 |  |  | Name: GROUND_FAULT; Label: Ground Fault Error; Value: 22 |  | Ground fault detected.
bitfield32 | ModEvt1 |  |  | Name: OPEN_DOOR_ERROR; Label: Open Door Error; Value: 23 |  | One or more doors are open.
bitfield32 | ModEvt1 |  |  | Name: RESERVED_3; Label: Reserved; Value: 24 |  | Reserved bit. | Do not implement.
bitfield32 | ModEvt1 |  |  | Name: RESERVED_4; Label: Reserved; Value: 25 |  | Reserved bit. | Do not implement.
bitfield32 | ModEvt1 |  |  | Name: RESERVED_5; Label: Reserved; Value: 26 |  | Reserved bit. | Do not implement.
bitfield32 | ModEvt1 |  |  | Name: FIRE_ALARM; Label: Fire Alarm; Value: 27 |  | A fire has been detected.
bitfield32 | ModEvt1 |  |  | Name: MODULE_CONFIGURATION_ALARM; Label: Configuation Alarm; Value: 28 |  | The battery module has been configured incorrectly and will not operate.
bitfield32 | ModEvt1 |  |  | Name: MODULE_CONFIGURATION_WARNING; Label: Configuation Warning; Value: 29 |  | The battery module has been configured incorrectly and may not operate as expected.
bitfield32 | ModEvt2 |  |  | Name: LEAK_ALARM; Label: Leak Alarm; Value: 0 |  | A leak has been detected.
bitfield32 | ModEvt2 |  |  | Name: PUMP_ALARM; Label: Pump Alarm; Value: 1 |  | A pump has experienced an alarm condition or some other error.
bitfield32 | ModEvt2 |  |  | Name: HIGH_PRESSURE_ALARM; Label: High Pressure Alarm; Value: 2 |  | Pressure exceeds maximum value.
bitfield32 | ModEvt2 |  |  | Name: HIGH_PRESSURE_WARNING; Label: High Pressure Warning; Value: 3 |  | Pressure approaching maximum value.
bitfield32 | ModEvt2 |  |  | Name: LOW_FLOW_ALARM; Label: Low Flow Alarm; Value: 4 |  | Flow exceeds minimum value.
bitfield32 | ModEvt2 |  |  | Name: LOW_FLOW_WARNING; Label: Low Flow Warning; Value: 5 |  | Flow approaching minimum value.
enum16 | ModConFail |  |  | Name: NO_FAILURE; Label: No Failure; Value: 0 |  | Connect did not fail.
enum16 | ModConFail |  |  | Name: BUTTON_PUSHED; Label: Button Pushed; Value: 1 |  | A button was pushed which prevented connection.
enum16 | ModConFail |  |  | Name: MODULE_GROUND_FAULT; Label: Ground Fault; Value: 2 |  | Ground fault during auto-connect.
enum16 | ModConFail |  |  | Name: OUTSIDE_VOLTAGE_RANGE; Label: Outside Voltage Range; Value: 3 |  | Outside voltage target window during auto-connect.
enum16 | ModConFail |  |  | Name: MODULE_NOT_ENABLED; Label: Module Not Enabled; Value: 4 |  | The module is not enabled.
enum16 | ModConFail |  |  | Name: FUSE_OPEN; Label: Fuse Open; Value: 5 |  | A fuse is open which prevents connection.
enum16 | ModConFail |  |  | Name: CONTACTOR_FAILURE; Label: Contactor Failure; Value: 6 |  | A contactor failed to operate.
enum16 | ModConFail |  |  | Name: PRECHARGE_FAILURE; Label: Precharge Failure; Value: 7 |  | A failure during precharge occurred.
enum16 | ModConFail |  |  | Name: MODULE_FAULT; Label: Module Fault; Value: 8 |  | A module fault has occurred. | See ModEvt1 and ModEvt2 for more information.
enum16 | ModSetEna |  |  | Name: ENABLE_MODULE; Label: Enable Module; Value: 1 |  | Enable the module.
enum16 | ModSetEna |  |  | Name: DISABLE_MODULE; Label: Disable Module; Value: 2 |  | Disable the module.
enum16 | ModSetCon |  |  | Name: CONNECT_MODULE; Label: Connect Module; Value: 1 |  | Connect the module.
enum16 | ModSetCon |  |  | Name: DISCONNECT_MODULE; Label: Disconnect Module; Value: 2 |  | Disconnect the module.
enum16 | ModDisRsn |  |  | Name: NONE; Label: No Reason; Value: 0 |  | No reason provided.
enum16 | ModDisRsn |  |  | Name: FAULT; Label: Fault; Value: 1 |  | A fault has occurred which caused the module to be disabled.
enum16 | ModDisRsn |  |  | Name: MAINTENANCE; Label: Maintenance; Value: 2 |  | The module has been disabled for maintenance reasons.
enum16 | ModDisRsn |  |  | Name: EXTERNAL; Label: External; Value: 3 |  | The module has been disabled by an external user or controller.
enum16 | ModDisRsn |  |  | Name: OTHER; Label: Other; Value: 4 |  | The module has been disabled for some other reason.

## 808
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Flow Battery Module Model | 808 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 1 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | ModuleTBD | Module Points To Be Determined |  | uint16 |  |  | R | M
Repeating Block |  | 3 | 0 | 1 | StackTBD | Stack Points To Be Determined |  | uint16 |  |  | R | M

## 809
Field Type | Applicable Point | Address Offset | Block Offset | Size | Name | Label | Value | Type | Units | SF | R/W | Mandatory M/O | Description | Notes
Header |  | 0 |  | 1 | ID | Flow Battery Stack Model | 809 | uint16 |  |  | R | M
Header |  | 1 |  | 1 | L |  | 1 + (RB Count * 1) | uint16 |  |  | R | M | Model Length
Fixed Block |  | 2 | 0 | 1 | StackTBD | Stack Points To Be Determined |  | uint16 |  |  | R | M
Repeating Block |  | 3 | 0 | 1 | CellTBD | Cell Points To Be Determined |  | uint16 |  |  | R | M